## Sheet1
Large Power Intervenors Information Request No. 15
GNTL Docket No. E015/CN-12-1163 |  |  | 2014-08-21
Assumptions | Docket No. E015/M-11-938 | Docket No. E015/CN-12-1163 | Comments
Line Voltage | 230 kV | 500 kV | Voltage increased to accommodate delivery of additional hydropower from MH to MP (133 MW ROA) and other utilities in the Upper Midwest, realize benefits of a new 500 kV tie line identified by MISO studies, provide MP customers with economy of scale capital cost reduction advantages, and provide a superior long-term solution for the region
Specific Route Identied | None | 2 options | Specific routes identified through 2 years of voluntary public outreach leading into development of the Route Permit Application
Specific Border Crossing Identifed | No | Yes | Border Crossing agreed to by Minnesota Power and Manitoba Hydro
Final Termination | Shannon 230 kV Substation | Blackbery 500 kV Substation | Blackberry provides more 230 kV outlet capability and better electrical performance for a 500 kV Project. Shannon is located adjacent to an active mine (Hibbtac) on leased property, meaning Project substation facilities would be subject to termination and relocation provisions in the lease agreement. Given the scale of investment in new substation facilities, this would be a significant risk.
Line Length (miles) | 194 | 220 | Total length increased due to termination at Blackberry instead of Shannon. Length of specific routes determined by 2 year routing process leading to Route Permit Application development
Route Permit Filed | No | Yes | Route Permit Filed on April 15, 2014
ROW Width (feet) | 130 | 200 | 500 kV Line requires a 200 ft ROW
Structure Type | H-Frame Wood | Steel Lattice Towers | Required ground clearances for a 500 kV line make wood structures uneconomical
Conductor Size | 954 ACSR | Tri-Bundled 1192 ACSR | Increased capacity of the line requires larger conductor. Electrical characteristics of 500 kV line require bundling of conductors.
Ownership | 100% MP | 100% MP | Minnesota Power must have a financial parter in this large capital outlay, MH will contribute CIAC in lieu of an ownership position*
Funding Obligation | 100% MP | 28.3% MP | Minnesota Power ratepayer should only be responsible for the PPA pro rata share of the GNTL
Other Owners | None | Manitoba Hydro | Manitoba Hydro must financially participate in this line as they will benefit from its construction
Capital Cost Assumptions | $190-240 Million (2018 Dollars) | $558-710 Million (2013 Dollars) | The cost of build a 500 kV project is significantly higher than a 230 kV project.
Capacity of the Line Consumed by PPA | 100% | 28.3% | The 250 MW PPA would use 100% of the 230 kV line while the same PPA delivered over the GNTL will required only a portion of the GNTL capacity
Capacity of the Line available for other transactions | 0% | 71.7% | A 230 kV project would allow for no additional transactions to occur while the GNTL will allow for additional transactions into the MISO market
MP's Share in 2013 Dollars | $163-204 Million | $158-201 Million | Minnesota Power rate payers should benefit from the economies of scale a large transmission line project creates. Apply similar environmental saferguards to the 230 kV project, the projected cost of the 230 kV option will increase to a range of $277 to $355 million in 2013 dollars
*MH may assign up to 49% of their financial obligation to another MISO TO, MP has approval rights to the assignment
LPI IR 015.1 Attachment